## Slide 1: Momentary vs Sustained Power Outage May 15, 2015

## Slide 2: Momentary and Sustained Power Outage
Sustained Power Outage
Total loss of power lasting more than two to five minutes
Can be due to accidental or planned reasons – storms, equipment damage etc.
Typically requires Utility’s intervention to restore power
Momentary Power Outage
Power loss of short duration (less than two to five minutes)
Often caused by interference on power lines – tree branch, dead animal etc.
Automatic “reclosers” on power lines revive power when interference gets cleared in few minutes

## Slide 3: Parameters Used in AMI to Determine Outage Type
Following configurable parameters are used in ORW’s AMI system
Threshold time to declare sustained outage
  Sustained power outage declared if voltage drops below threshold for this amount of time
  Default value = 120 seconds. Configurable setting
Minimum duration of steady power required
  Power is considered restored if it is observed for this entire duration
  Default value = 3000ms. Configurable setting
Observance window of power restoration activity
  Sustained outage declared if no power restoration activity occurs with in this time
  Sliding window that is reset when restoration attempts (by recloser) occurs
  Quicker sustained outage detection
  Default value = 60 seconds. Configurable setting

## Slide 4: Momentary Outage & Blink Counts
Power outage
Fast operation
(closed)
Reclosing interval
(open)
Threshold Time for Sustained Outage
Reclose Time
Power restoration
Blink Count = 3
Power is restored before expiry of observance window time or threshold time
Observance Window
(sliding)

## Slide 5: Sustained Outage: Expiry of Threshold Time
Threshold Time for Sustained Outage
Power outage
Fast operation
(closed)
Reclosing interval
(open)
Delayed operation
(closed)
Recloser Lockout
(open)
Reclose Time
Observance Window
(sliding)
Sustained Outage
Determined
Expiry of timer
Sustained outage: If outage duration > threshold time for sustained outage
Reclose Time

## Slide 6: Sustained Outage: Expiry of Observance Timer
Power outage
Fast operation
(closed)
Reclosing interval
(open)
Recloser Lockout
(open)
Sustained Outage
Determined
Expiry of timer
Observance Window
Threshold Time for Sustained Outage
Reclose Time
Early detection of recloser lockout  Early declaration of sustained outage

## Slide 7: Distinguishing Momentary vs Sustained Outages
Three configurable parameters available in AMI system to determine and distinguish momentary outage from sustained outage
If power is restored before a sustained power outage is declared, then it is considered a momentary power outage
Sustained outages are reported immediately as alarms (email alerts)
Momentary outages are logged and reported every 15 minutes (no emails)
Configurable AMI Parameter | Current Default | Requirement
Threshold time to declare sustained outage | 120 seconds | Should be less than 5 minutes to allow Last Gasp message transmission
Minimum duration of steady power required | 3000 ms | Should be greater than the duration of recloser “reclose time”
Observance window of power restoration activity | 60 seconds* | Should be greater than the “reclosing interval”
*Default for SGM3000 meters in 125 seconds

## Slide 8: Questions for Utility
How long of a continuous loss of power is considered as a sustained outage? E.g., 2 minutes?
What voltage level below normal constitutes a loss of power? E.g., 75%?
What is the typical duration of a recloser attempt? E.g., 500ms?
Does the duration of reclosing change with each attempt? If so, what is the length of longest recloser attempt?
Does the reclosing interval – i.e., time between each recloser attempt – increase after each reclosing attempt? E.g. 1st attempt in 2-5s, 2nd attempt in 10s, 3rd attempt in 45s, etc.
What is the length of the longest reclosing interval?
How many attempts does the reclosure make to restore power?
Momentary Outage: If a recloser makes 3 attempts before power is restored, does this constitute as
  3 blink counts (3 reclosing intervals) or 1 blink count (1 momentary outage)

## Slide 9: Thank You!

## Slide 10: Old questionnaire for Utility
How much time with loss of power constitutes a sustained outage?
What is the typical duration within which a sustained outage has to be determined?
How long does a typical reclosing attempt duration last?
Does the duration for which recloser closes change with each attempt? If so, how long is the duration of closing for each attempt?
Does the reclosing interval – i.e., time between recloser attempts – increase with each reclosing attempt?
What is the range for reclosing interval? How much is it for each attempt?
How many attempts does the reclosure make to restore power?
Momentary Outage: If a recloser makes 2 attempts before power is restored, does this constitute as
  3 blink counts (3 reclosing intervals) or 1 blink count (1 momentary outage)

## Slide 11: EMCM Operation in Outage Detection
Power outage
Recloser
(closed)
Reclosing interval
(open)
Recloser Lockout
(open)
Reclose Time
Meter
EMCM
Node
Power fail
assert
Power fail
assert
Save timestamp
Enter low power mode
Power fail
confirm
Outage detection
Back off
Last Gasp
Notification
Enter low power mode
Sustained outage detected

## Slide 12: Power Restoration Notification
Power restored
Meter
EMCM
Node
Power fail
deassert
Power
restored
Reports exact time of
Power restoration
Power_Restore
Node rejoins the
AMI network
Power_Fail_Clear
Notifies power
restoration
HES/OTV
Power restoration
Notification
(CIM message)
Power restoration
Details
(CIM message)
OMS